## EXPLANATION
GUIDELINES FOR COMBINING MASTERDRIVES AND SINAMICS HARDWARE ON A COMMON DC BUS
NOTE: Siemens recommends that you try to avoid mixing MASTERDRIVES and SINAMICS hardware on the same DC bus.
However, this is not always practical, so the following guidelines should be considered when attempting this task.
1) It is acceptable to use MASTERDRIVES braking units and resistors on systems with SINAMICS hardware.
The MASTERDRIVES braking unit is an autonomous part that can be used with SINAMICS S120 in most systems.
You should select the MASTERDRIVES braking unit and resistor that most closely matches the recommended SINAMICS components in kW and Ohms
2) It is possible to replace existing MASTERDRIVES rectifiers, regen rectifiers or Active Front Ends with SINAMICS BLMs, SLMs or ALMs.
MASTERDRIVES rectifiers and regen rectifiers do not have any internal capacitance.
BLMs, SLMs and ALMs have an internal capacitance value which adds to the total capacitance on the DC bus.
BLMs, SLMs and ALMs also have a maximum connected capacitance value that must not be exceeded in order to provide proper operation and avoid damaging the pre-charge circuit.
Use the work sheet on the next tab to determine if the proposed BLM, SLM or ALM can handle the total capacitance of the bus.
STEP 1: Enter a '1' in the quantity column for the desired BLM, SLM or ALM you wish to use
STEP 2: Enter the proper quanities for all existing and new drives connected to the DC bus
STEP 3: Click on the SORT button
STEP 4: If the cell under the "Capacitance Limit for Drive Lineup" turns red, the capacitance of the connected drives exceeds the limit on the BLM, SLM or ALM
3) There is more risk for scenarios where MASTERDRIVES inverters are replaced with SINAMICS S120 motor modules.
Since S120 motor modules have about 50% less capacitance than equivalent MASTERDRIVES, the total bus capacitance is lowered with each substitution.
There is a risk of having insufficient bus capacitance, which can shorten the life of the capacitors or result in capacitor explosions in the worst cases.
SINAMICS S120 motor modules must also be interlocked to the rectifier / line module to assure they are not enabled until the DC bus is operational.
If you are considering this substitution, you should gather the part numbers of all components connected to your DC bus and consult Siemens for support.

## CAPACITANCE
|  | Note: These values are only valid for 60Hz at 480V | Capacitance per unit (uF) | Total System Capacitance (uF) | Capacitance Limit for Drive Lineup (uF)
QTY | PART NUMBER | DESCRIPTION |  | 0 | 0
| BLM | BASIC LINE MODULES
| 6SL3130-1TE22-0AA0 | Basic Line Module; 20kW; 100mm wide | 940 | 0 | 20000
| 6SL3130-1TE24-0AA0 | Basic Line Module; 40kW; 150mm wide | 1880 | 0 | 20000
| 6SL3130-1TE31-0AA0 | Basic Line Module; 100kW; 200mm wide | 4100 | 0 | 50000
| 6SL3330-1TE34-2AA0 | Basic Line Module Chassis;200kW; 365A; FB | 7200 | 0 | 57600
| 6SL3330-1TE35-3AA0 | Basic Line Module Chassis;250kW; 460A; FB | 9600 | 0 | 76800
| 6SL3330-1TE38-2AA0 | Basic Line Module Chassis;400kW; 710A; FB | 14600 | 0 | 116800
| 6SL3330-1TE41-2AA0 | Basic Line Module Chassis;560kW; 1010A; GB | 23200 | 0 | 185600
| 6SL3330-1TE41-5AA0 | Basic Line Module Chassis;710kW; 1265A; GB | 29000 | 0 | 232000
| SLM | SMART LINE MODULES
| 6SL3130-6AE15-0AB0 | Smart Line Module;5kW; 12A; 50mm wide | 220 | 0 | 6000
| 6SL3130-6AE21-0AB0 | Smart Line Module;10kW; 24A; 50mm wide | 330 | 0 | 6000
| 6SL3130-6TE21-6AA3 | Smart Line Module;16kW; 26A; 100mm wide | 710 | 0 | 20000
| 6SL3130-6TE23-6AA3 | Smart Line Module;36kW; 58A; 150mm wide | 1410 | 0 | 20000
| 6SL3330-6TE35-5AA0 | Smart Line Module Chassis; 250kW; 463A; FG | 8400 | 0 | 33600
| 6SL3330-6TE37-3AA0 | Smart Line Module Chassis; 355kW; 614A; FG | 12000 | 0 | 48000
| 6SL3330-6TE41-1AA0 | Smart Line Module Chassis; 500kW; 883A; FH | 16800 | 0 | 67200
| 6SL3330-6TE41-3AA0 | Smart Line Module Chassis; 630kW; 1093A; FJ | 18900 | 0 | 75600
| 6SL3330-6TE41-7AA0 | Smart Line Module Chassis; 800kW; 1430A; FJ | 28800 | 0 | 115200
| ALM | ACTIVE LINE MODULES
| 6SL3130-7TE21-6AA3 | Active Line Module; 16kW; 26A; 100mm wide | 710 | 0 | 20000
| 6SL3130-7TE23-6AA3 | Active Line Module; 36kW; 58A; 150mm wide | 1410 | 0 | 20000
| 6SL3130-7TE25-5AA3 | Active Line Module; 55kW; 88A; 200mm wide | 1880 | 0 | 20000
| 6SL3130-7TE28-0AA3 | Active Line Module; 80kW; 128A; 300mm wide | 2820 | 0 | 20000
| 6SL3130-7TE31-2AA3 | Active Line Module; 120kW; 192A; 300mm wide | 3995 | 0 | 20000
| 6SL3330-7TE32-1AA0 | Active Line Module; 132kW; 210A; Chassis (AIM Limit) | 4200 | 0 | 20800
| 6SL3330-7TE32-6AA0 | Active Line Module; 160kW; 260A; Chassis (AIM Limit) | 5200 | 0 | 20800
| 6SL3330-7TE33-8AA0 | Active Line Module; 235kW; 380A; Chassis (AIM Limit) | 7800 | 0 | 38400
| 6SL3330-7TE35-0AA0 | Active Line Module; 300kW; 490A; Chassis (AIM Limit) | 9600 | 0 | 38400
| 6SL3330-7TE36-1AA0 | Active Line Module; 380kW; 605A; Chassis (AIM Limit) | 12600 | 0 | 67200
| 6SL3330-7TE38-4AA0 | Active Line Module; 500kW; 840A; Chassis (AIM Limit) | 16800 | 0 | 67200
| 6SL3330-7TE41-0AA0 | Active Line Module; 630kW; 985A; Chassis (AIM Limit) | 18900 | 0 | 115200
| 6SL3330-7TE41-4AA0 | Active Line Module; 900kW; 1405A; Chassis (AIM Limit) | 28800 | 0 | 115200
CAPACITOR MODULE
| 6SL3100-1CE14-0AA0 | Capacitor Module | 4000 | 0
S120 - SINGLE AXIS MOTOR MODULE
| 6SL3120-1TE13-0AA3 | 1-Axis MoMo; 3A; 1.6kW; DC/AC; 50mm | 110 | 0
| 6SL3120-1TE15-0AA3 | 1-Axis MoMo; 5A; 2.7kW; DC/AC; 50mm | 110 | 0
| 6SL3120-1TE21-0AA3 | 1-Axis MoMo; 9A; 4.8kW; DC/AC; 50mm | 110 | 0
| 6SL3120-1TE21-8AA3 | 1-Axis MoMo; 18A; 9.7kW; DC/AC; 50mm | 220 | 0
| 6SL3120-1TE23-0AA3 | 1-Axis MoMo; 30A; 16kW; DC/AC; 100mm | 705 | 0
| 6SL3120-1TE24-5AA3 | 1-Axis MoMo; 45A; 24kW; DC/AC; 150mm | 1175 | 0
| 6SL3120-1TE26-0AA3 | 1-Axis MoMo; 60A; 32kW; DC/AC; 150mm | 1410 | 0
| 6SL3120-1TE28-5AA3 | 1-Axis MoMo; 85A; 46kW; DC/AC; 200mm | 1880 | 0
| 6SL3120-1TE31-3AA3 | 1-Axis MoMo; 132A; 71kW; DC/AC; 300mm | 2820 | 0
| 6SL3120-1TE32-0AA3 | 1-Axis MoMo; 200A; 107kW; DC/AC; 300mm | 3995 | 0
| 6SL3320-1TE32-1AA0 | 1-Axis MoMo; 210A; 110kW; DC/AC; FX Chassis | 4200 | 0
| 6SL3320-1TE32-6AA0 | 1-Axis MoMo; 260A; 132kW; DC/AC; FX Chassis | 5200 | 0
| 6SL3320-1TE33-1AA0 | 1-Axis MoMo; 310A; 160kW; DC/AC; GX Chassis | 6300 | 0
| 6SL3320-1TE33-8AA0 | 1-Axis MoMo; 380A; 200kW; DC/AC; GX Chassis | 7800 | 0
| 6SL3320-1TE35-0AA0 | 1-Axis MoMo; 490A; 250kW; DC/AC; GX Chassis | 9600 | 0
| 6SL3320-1TE36-1AA0 | 1-Axis MoMo; 605A; 315kW; DC/AC; HX Chassis | 12600 | 0
| 6SL3320-1TE37-5AA0 | 1-Axis MoMo; 745A; 400kW; DC/AC; HX Chassis | 15600 | 0
| 6SL3320-1TE38-4AA0 | 1-Axis MoMo; 840A; 450kW; DC/AC; HX Chassis | 16800 | 0
| 6SL3320-1TE41-0AA0 | 1-Axis MoMo; 985A; 560kW; DC/AC; JX Chassis | 18900 | 0
| 6SL3320-1TE41-2AA0 | 1-Axis MoMo; 1260A; 710kW; DC/AC; JX Chassis | 26100 | 0
| 6SL3320-1TE41-4AA0 | 1-Axis MoMo; 1405A; 800kW; DC/AC; JX Chassis | 28800 | 0
S120 - BOOKSIZE DUAL AXIS MOTOR MODULE
| 6SL3120-2TE13-0AA3 | 2-Axis MoMo; 2 x 3A; 1.6kW; DC/AC; 50mm | 110 | 0
| 6SL3120-2TE15-0AA3 | 2-Axis MoMo; 2 x 5A; 2.7kW; DC/AC; 50mm | 220 | 0
| 6SL3120-2TE21-0AA3 | 2-Axis MoMo; 2 x 9A; 4.8kW; DC/AC; 50mm | 220 | 0
| 6SL3120-2TE21-8AA3 | 2-Axis MoMo; 2 x 18A; 9.7kW; DC/AC; 100mm | 705 | 0
MASTERDRIVES VC
| 6SE7012-0TP60 | VC Inc;DC/AC;0.75kW;Compact+;510-650V;2.0A | 100 | 0
| 6SE7014-0TP60 | VC Inc;DC/AC;1.5kW;Compact+;510-650V;4.0A | 100 | 0
| 6SE7016-0TP60 | VC Inc;DC/AC;2.2kW;Compact+;510-650V;6.1A | 200 | 0
| 6SE7021-0TP60 | VC Inc;DC/AC;4kW;Compact+;510-650V;10.2A | 300 | 0
| 6SE7021-3TP60 | VC Inc;DC/AC;5.5kW;Compact+;510-650V;13.2A | 600 | 0
| 6SE7021-8TP60 | VC Inc;DC/AC;7.5kW;Compact+;510-650V;17.5A | 600 | 0
| 6SE7022-6TP60 | VC Inc;DC/AC;11kW;Compact+;510-650V;25.5A | 1100 | 0
| 6SE7023-4TP60 | VC Inc;DC/AC;15kW;Compact+;510-650V;34A | 1100 | 0
| 6SE7023-8TP60 | VC Inc;DC/AC;18.5kW;Compact+;510-650V;37.5A | 2200 | 0
| 6SE7024-7TP60 | VC Inc;DC/AC;22kW;Compact+;510-650V;47A | 2200 | 0
| 6SE7026-0TP60 | VC Inc;DC/AC;30kW;Compact+;510-650V;59A | 3300 | 0
| 6SE7027-2TP60 | VC Inc;DC/AC;37kW;Compact+;510-650V;72A | 3300 | 0
| 6SE7016-1TA61 | VC Inc;DC/AC;2.2kW;Compact;510-650V;6.1A | 200 | 0
| 6SE7018-0TA61 | VC Inc;DC/AC;3kW;Compact;510-650V;8A | 300 | 0
| 6SE7021-0TA61 | VC Inc;DC/AC;4kW;Compact;510-650V;10.2A | 300 | 0
| 6SE7021-3TB61 | VC Inc;DC/AC;5.5kW;Compact;510-650V;13.2A | 600 | 0
| 6SE7021-8TB61 | VC Inc;DC/AC;7.5kW;Compact;510-650V;17.5A | 600 | 0
| 6SE7022-6TC61 | VC Inc;DC/AC;11kW;Compact;510-650V;25.5A | 1100 | 0
| 6SE7023-4TC61 | VC Inc;DC/AC;15kW;Compact;510-650V;34A | 1100 | 0
| 6SE7023-8TD61 | VC Inc;DC/AC;18.5kW;Compact;510-650V;37.5A | 2200 | 0
| 6SE7024-7TD61 | VC Inc;DC/AC;22kW;Compact;510-650V;47A | 2200 | 0
| 6SE7026-0TD61 | VC Inc;DC/AC;30kW;Compact;510-650V;59A | 3300 | 0
| 6SE7027-2TD61 | VC Inc;DC/AC;37kW;Compact;510-650V;72A | 3300 | 0
| 6SE7031-0TE60 | VC Inc;DC/AC;45kW;Chassis;510-650V;92A | 5000 | 0
| 6SE7031-2TF60 | VC Inc;DC/AC;55kW;Chassis;510-650V;124A | 7500 | 0
| 6SE7031-5TF60 | VC Inc;DC/AC;75kW;Chassis;510-650V;146A | 10000 | 0
| 6SE7031-8TF60 | VC Inc;DC/AC;90kW;Chassis;510-650V;186A | 10000 | 0
| 6SE7032-1TG60 | VC Inc;DC/AC;110kW;Chassis;510-650V;210A | 10000 | 0
| 6SE7032-6TG60 | VC Inc;DC/AC;132kW;Chassis;510-650V;260A | 12500 | 0
| 6SE7033-2TG60 | VC Inc;DC/AC;160kW;Chassis;510-650V;315A | 12500 | 0
| 6SE7033-7TG60 | VC Inc;DC/AC;200kW;Chassis;510-650V;370A | 15000 | 0
| 6SE7035-1TJ60 | VC Inc;DC/AC;250kW;Chassis;510-650V;510A | 27000 | 0
| 6SE7036-0TJ60 | VC Inc;DC/AC;315kW;Chassis;510-650V;590A | 34000 | 0
| 6SE7037-0TJ60 | VC Inc;DC/AC;400kW;Chassis;510-650V;690A | 36000 | 0
| 6SE7038-6TK60 | VC Inc;DC/AC;500kW;Chassis;510-650V;860A | 45000 | 0
| 6SE7041-1TK60 | VC Inc;DC/AC;630kW;Chassis;510-650V;1100A | 63000 | 0
| 6SE7041-3TL60 | VC Inc;DC/AC;710kW;Chassis;510-650V;1300A | 79000 | 0
MASTERDRIVES MC
| 6SE7012-0TP50 | MC Inc;DC/AC;0.75kW;Compact+;510-650V;2.0A | 100 | 0
| 6SE7014-0TP50 | MC Inc;DC/AC;1.5kW;Compact+;510-650V;4.0A | 100 | 0
| 6SE7016-0TP50 | MC Inc;DC/AC;2.2kW;Compact+;510-650V;6.1A | 200 | 0
| 6SE7021-0TP50 | MC Inc;DC/AC;4kW;Compact+;510-650V;10.2A | 300 | 0
| 6SE7021-3TP50 | MC Inc;DC/AC;5.5kW;Compact+;510-650V;13.2A | 600 | 0
| 6SE7021-8TP50 | MC Inc;DC/AC;7.5kW;Compact+;510-650V;17.5A | 600 | 0
| 6SE7022-6TP50 | MC Inc;DC/AC;11kW;Compact+;510-650V;25.5A | 1100 | 0
| 6SE7023-4TP50 | MC Inc;DC/AC;15kW;Compact+;510-650V;34A | 1100 | 0
| 6SE7023-8TP50 | MC Inc;DC/AC;18.5kW;Compact+;510-650V;37.5A | 2200 | 0
| 6SE7024-7TP50 | MC Inc;DC/AC;22kW;Compact+;510-650V;47A | 2200 | 0
| 6SE7026-0TP50 | MC Inc;DC/AC;30kW;Compact+;510-650V;59A | 3300 | 0
| 6SE7027-2TP50 | MC Inc;DC/AC;37kW;Compact+;510-650V;72A | 3300 | 0
| 6SE7016-1TA51 | MC Inc;DC/AC;2.2kW;Compact;510-650V;6.1A | 200 | 0
| 6SE7018-0TA51 | MC Inc;DC/AC;3kW;Compact;510-650V;8A | 300 | 0
| 6SE7021-0TA51 | MC Inc;DC/AC;4kW;Compact;510-650V;10.2A | 300 | 0
| 6SE7021-3TB51 | MC Inc;DC/AC;5.5kW;Compact;510-650V;13.2A | 600 | 0
| 6SE7021-8TB51 | MC Inc;DC/AC;7.5kW;Compact;510-650V;17.5A | 600 | 0
| 6SE7022-6TC51 | MC Inc;DC/AC;11kW;Compact;510-650V;25.5A | 1100 | 0
| 6SE7023-4TC51 | MC Inc;DC/AC;15kW;Compact;510-650V;34A | 1100 | 0
| 6SE7023-8TD51 | MC Inc;DC/AC;18.5kW;Compact;510-650V;37.5A | 2200 | 0
| 6SE7024-7TD51 | MC Inc;DC/AC;22kW;Compact;510-650V;47A | 2200 | 0
| 6SE7026-0TD51 | MC Inc;DC/AC;30kW;Compact;510-650V;59A | 3300 | 0
| 6SE7027-2TD51 | MC Inc;DC/AC;37kW;Compact;510-650V;72A | 3300 | 0
| 6SE7031-0TE50 | MC Inc;DC/AC;45kW;Chassis;510-650V;92A | 5000 | 0
| 6SE7031-2TF50 | MC Inc;DC/AC;55kW;Chassis;510-650V;124A | 7500 | 0
| 6SE7031-8TF50 | MC Inc;DC/AC;75kW;Chassis;510-650V;155A | 10000 | 0
| 6SE7032-1TG50 | MC Inc;DC/AC;90kW;Chassis;510-650V;175A | 10000 | 0
| 6SE7032-6TG50 | MC Inc;DC/AC;110kW;Chassis;510-650V;218A | 10000 | 0
| 6SE7033-2TG50 | MC Inc;DC/AC;132kW;Chassis;510-650V;262A | 12500 | 0
| 6SE7033-7TG50 | MC Inc;DC/AC;160kW;Chassis;510-650V;308A | 15000 | 0
| 6SE7035-1TJ50 | MC Inc;DC/AC;200kW;Chassis;510-650V;423A | 27000 | 0
| 6SE7036-0TJ50 | MC Inc;DC/AC;250kW;Chassis;510-650V;491A | 34000 | 0
Note on F2: If this cell is red, capacitance of drive lineup is too much for line module