Safety lighting			
	
Is a fire protection concept requiring safety lighting available?			Yes		No	
How many fire areas does the project have?			
Is the estate a building structure for gatherings of people in compliance with DIN EN 50172 
(place of public assembly, guest accommodation facility high-rise building, shop, workplace etc.)?			Yes		No	
Have requirements imposed by state building code, safety at work legislation, workplace regulations, building regulations, etc. been considered?	
Rated operating time		h	
Switchover times		s	
Illuminance		lx	
Safety lighting already required during ongoing construction work?			Yes		No	
Other	

	
			
Special environmental requirements (higher degree of protection, explosion-prone area, aggressive gases, etc.)	
	
Has a danger assessment been made 
(e.g. for workplaces by the relevant Employer's Liability Insurance Association)?			Yes		No	
Have escape routes been specified 
(are there any escape route plans)?			Yes		No	
Have the locations of firefighting equipment, alarm stations and first aid points been determined?			Yes		No	
Shall the safety lighting be integrated into the normal lighting system (higher power requirements, provisions for switched permanent light necessary)?			Yes		No	
Operating mode selection			
	Permanent operation			
	Standby operation			
	Combination of permanent and standby operation			
Has voltage monitoring of the sub-distribution board for normal supply been included in the planning for standby operation?			Yes		No	
In case of standby operation, shall normal power supply be monitored at the main distribution board for safety lighting (exception: single-battery system)?			Yes		No	
Is remote signaling to a permanently occupied desk intended (exception: single-battery system)?			Yes		No	
			
Type of power supply system			
	CPS		LPS			EB		AE	
	BS					
For CPS and LPS please note:			
Can the battery room be aired/vented to the outside?			Yes		No	
Is a charging booster required 
(manufacturer's specification)?			Yes		No	
Are luminaries and electronic control gear suitable for battery systems (voltage: 183.6 V – 259.2 V DC and firing behavior)?			Yes		No	
For CPS please note:			
Does a self-contained battery room exist?			Yes		No	
Installation of main distribution board:			
Shall the main distribution board for safety power supply (and battery, if applicable) be installed in a separate room – are walls and ceilings fire resistant (F90); is the door fire-retardant (T30)?			Yes		No	
Installation sub-distribution board:			
Shall the sub-distribution board for safety power supply be installed in a separate F30 room or type-tested E30 enclosure?			Yes		No	
Do the wiring systems meet the fire protection requirements?			Yes		No	
Which light spot heights are available 
(selection criterion for luminaire type)?		m	
Alternating luminaire assignment to at least two independent protection devices?			Yes		No	

With the completed list you have gained an overview of the project.
Do you need detailed information e.g. about concept development or budget estimation?
With the data contained in the checklist, contact your responsible TIP contact person:	
Totally Integrated Power supports electrical designers in different planning stages with software tools, Revit files for Building Information Modeling (BIM), tender specification texts, planning and application manuals and professional consulting by our experienced technical specialists in many countries: www.siemens.com/tip-cs

Get in touch with us: www.siemens.com/tip-cs/contact